# System Requirements Specification

Product: Industrial Controller X200 (Series B)
Document Ref: SRS-2026-X200-EU | Version: 2.4 | Status: Approved
Author: Atlas Motion Systems — Systems Engineering Division
Applicable Directives: 2014/30/EU (EMC), 2014/35/EU (LVD), 2006/42/EC (Machinery)

# 1. Scope and System Overview

The Industrial Controller X200 is an embedded, DIN-rail mounted real-time automation controller designed for high-reliability motion control, robotic cell coordination, and critical industrial telemetry. This specification establishes mandatory engineering requirements, functional criteria, electrical ratings, and safety boundaries for CE compliance and industrial deployment.

# 2. Applicable Harmonized Standards

| Standard Ref | Title | Compliance Target |
| --- | --- | --- |
| IEC 61010-1:2010+A1:2016 | Safety requirements for electrical equipment for measurement & control | Mandatory (Class I) |
| EN 61326-1:2021 | EMC requirements — Equipment for control and laboratory use (Industrial) | Zone B Industrial |
| ISO 13849-1:2023 | Safety of machinery — Safety-related parts of control systems | PL d, Cat 3 |
| IEC 60529:2013 | Degrees of protection provided by enclosures (IP Code) | IP65 Enclosure |

# 3. Electrical Specifications & Power Budget

REQ-ELE-001 [Critical]: Nominal Operating Voltage and Range
The controller shall operate continuously from a regulated DC input supply with a nominal voltage of 24.0 V DC. The system must remain fully functional across an input tolerance range of 18.0 V DC to 30.0 V DC (24V DC -25% / +25%) with transient overvoltage withstand up to 36.0 V DC for durations ≤ 500 ms.

REQ-ELE-002 [High]: Maximum Power Consumption & Inrush Current
Under maximum continuous processing and full digital/analog I/O load (32 channels energized), total system power consumption shall not exceed 45.0 W. Peak inrush current during cold-start boot sequence shall be limited to ≤ 8.0 A for a duration not exceeding 10.0 ms.

REQ-ELE-003 [Critical]: Galvanic Isolation and Dielectric Withstand
All primary field-bus I/O channels, Ethernet interfaces, and internal 3.3V/5V logic power planes shall feature galvanic optical and magnetic isolation. The insulation barrier shall withstand a test voltage of 2.5 kV AC RMS (50/60 Hz) for 60 seconds without dielectric breakdown, and maintain leakage current < 1.0 mA.

REQ-ELE-004 [High]: Internal DC Bus Ripple and Noise
The internal filtered DC power rail distributed to high-speed analog acquisition stages shall exhibit peak-to-peak ripple and noise not exceeding 50.0 mV pk-pk across a 20 MHz measurement bandwidth under 100% load.

# 4. Environmental & Climatic Requirements

REQ-ENV-001 [High]: Operating Ambient Temperature Range
The equipment shall maintain full functional performance and timing accuracy across an ambient operating temperature range of -20.0 °C to +55.0 °C under continuous convection cooling without forced airflow.

REQ-ENV-002 [Medium]: Storage and Transport Temperature Limits
The equipment, in non-energized packed state, shall withstand storage temperatures from -40.0 °C to +85.0 °C and relative humidity levels up to 95.0% non-condensing (at +40.0 °C for 96 hours).

REQ-ENV-003 [High]: Ingress Protection (IP Rating)
When installed inside a sealed industrial enclosure with properly torqued gland connectors, the front-panel user interface and sealed bezel shall provide IP65 ingress protection according to IEC 60529 (dust-tight and protection against water jets from any direction).

# 5. Functional Safety & Real-Time Performance

REQ-SAF-001 [Critical]: Emergency Stop (E-Stop) Response Time
Upon actuation of the dual-channel emergency stop circuit (Safe Torque Off - STO), the system shall de-energize all motion control drive gate signals within a maximum deterministic latency of ≤ 25.0 ms (target ≤ 20.0 ms).

REQ-SAF-002 [Critical]: Dual-Channel Redundancy & Diagnostic Coverage
The safety supervisory micro-controller shall achieve diagnostic coverage (DC) ≥ 99.0% and mean time to dangerous failure (MTTFd) ≥ 100 years, satisfying Category 3 / Performance Level d (PL d) per ISO 13849-1.

REQ-COM-001 [Medium]: Real-Time EtherCAT Cycle Jitter
The industrial Ethernet interface operating in EtherCAT master mode shall support a deterministic cycle time of 1.0 ms with maximum allowable cycle jitter ≤ 15.0 microseconds across 1,000,000 consecutive communication frames.